## Slide 1: Project Presentation
EEE 306
Power System Laboratory
Group: 06

## Slide 2
Load Flow Analysis on
IEEE 39 Bus System at 50Hz

## Slide 3
Solution Steps
Step 01:
Simulating the system with Given Data , with out any DC Line, Induction Motors, TCUL Xmer
Simulation result
No Overloading Occurred.
Couple of Line underloading and under loaded Transformer was observed

## Slide 4
Step 02:
Simulating the system with Given Data , with a DC Line, Induction Motors, TCUL Xmer, Removing L15 AC line
Simulation result
Some bus was out of their voltage limit
At L22, L14, L17,l07,L18,L09 line Overloading Occurred.
Transformer 03 was highly overloaded
G03,G06,G07 crossed their Reactive Limits

## Slide 5
Step 03:
Simulation result
No Gen has crossed their Reactive Limits
Some bus was out of their voltage limit
Transformer 03 was overloaded as before
Line Overloading remained same
To solve Generators at reactive limits problem, one SVC was connected B23
Explanation
Generator 07, connected at B23, were consuming highly reactive power than reactive limits. SVC can absorb or deliver reactive power . So, one SVC was connected at B23. G07 problem was solved as well as G03,G06.

## Slide 6
Step 04:
Simulation result
No Gen has crossed their Reactive Limits
No buses were out of their voltage limits
Transformer 03 was overloaded as before
Line Overloading L22, L07, L18,L09
To solve bus out of voltage limit , One SVC was connected B09
Explanation
Some buses were out of voltage limits. There voltage (pu) was less than minimum. So , SVC was connected at B09, to deliver reactive power . Thus, bus voltage increased and problems are solved.

## Slide 7
Step 05:
Simulation result
No Transformer overloading problem was occured
Line Overloading remains same L22, L07, L09
To solve the transformer overloading problem, active generation of G01, G03, G10 was increased by 50MW.
Explanation
T03 was connected between B31 and B06. Again, B31 is slack bus. Again, B06 is very closed to B31. So, high power is flowing through T03. To solve this, we have to increase the generation of some other generator, to release pressure of swing generator

## Slide 8
Step 06:
Simulation result
Line overloading problem solved at L07
Line Overloading remains same as L22, L09
To solve line overloading problem , two more svc was connected at B04 and B05
Explanation
L07 was connected between B04 and B05, So, we have attached SVC at both side

## Slide 9
Step 07:
Simulation result
To solve L22 and L09 overloading problem we have increased the loading limit of L09 up to 1200,and L22 at 1800
After this step, only line underloading and transformer underloading was remained
By decreasing the loading limit of line , under loading problem of line was also solved

## Slide 10
Contributions
1706150: Data entry
1706145: Data entry and cross-checking
1706149: Placing corrective devices and problems solving and making presentation slide
1706189:Placing corrective devices and problems solving

## Slide 11
After
Step 02

## Slide 12
After
Step 03

## Slide 13
After
Step 04

## Slide 14
After
Step 05

## Slide 15
After
Step 06

## Slide 16
After step 07