## after step 02
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
B10 | 0 | 345 | 0.9 | 1.1 | 0.897 | -14.6
B11 | 0 | 345 | 0.9 | 1.1 | 0.884 | -14.8
B12 | 0 | 138 | 0.9 | 1.1 | 0.866 | -15.7
B13 | 0 | 345 | 0.9 | 1.1 | 0.891 | -16.4
B14 | 0 | 345 | 0.9 | 1.1 | 0.886 | -20.7
B04 | 0 | 345 | 0.9 | 1.1 | 0.872 | -22.9
B05 | 0 | 345 | 0.9 | 1.1 | 0.856 | -16.3
B06 | 0 | 345 | 0.9 | 1.1 | 0.863 | -15
B07 | 0 | 345 | 0.9 | 1.1 | 0.829 | -16.6
B08 | 0 | 345 | 0.9 | 1.1 | 0.818 | -16.5
B09 | 0 | 345 | 0.9 | 1.1 | 0.719 | 1.8
B9_INV | 0 | 100 | 0.9 | 1.1 | 0.707 | 5.8
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L22 | B16 | B19 | 10.6 | 7.768 | 14.939
L14 | B08 | B09 | 7.139 | 5.976 | 8.963
L17 | B10 | B13 | 6.414 | 5.976 | 8.963
L07 | B04 | B05 | 7.773 | 5.976 | 8.963
L18 | B13 | B14 | 6.614 | 5.976 | 8.963
L09 | B05 | B06 | 8.356 | 5.976 | 8.963
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L20 | B15 | B16 | 2.945 | 2.988
L30 | B25 | B26 | 0.292 | 2.988
L31 | B26 | B27 | 2.512 | 2.988
L12 | B06 | B11 | 2.626 | 2.988
L32 | B26 | B28 | 1.514 | 2.988
L13 | B07 | B08 | 2.528 | 2.988
L23 | B16 | B21 | 1.388 | 2.988
L33 | B26 | B29 | 1.991 | 2.988
L25 | B17 | B18 | 1.675 | 2.988
L16 | B10 | B11 | 2.934 | 2.988
L26 | B17 | B27 | 1.728 | 2.988
L06 | B03 | B18 | 0.105 | 2.988
L27 | B21 | B22 | 2.779 | 3.884
L08 | B04 | B14 | 2.849 | 2.988
L29 | B23 | B24 | 0.341 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
T03 | B06 | B31 | 924.032 | 800 | 850
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 396.843 | 550
T01 | B12 | B11 | 45.67 | 250
T02 | B12 | B13 | 55.555 | 250
T12 | B19 | B20 | 377.276 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
G03 | B32 | 650 | 453.53 | -192 | 448
G06 | B35 | 650 | 579.01 | -192 | 448
G07 | B36 | 560 | 520.31 | -168 | 392
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]

## after step 03
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
B11 | 0 | 345 | 0.9 | 1.1 | 0.892 | -14.6
B12 | 0 | 138 | 0.9 | 1.1 | 0.874 | -15.4
B13 | 0 | 345 | 0.9 | 1.1 | 0.9 | -16.1
B14 | 0 | 345 | 0.9 | 1.1 | 0.898 | -20.3
B04 | 0 | 345 | 0.9 | 1.1 | 0.883 | -22.5
B05 | 0 | 345 | 0.9 | 1.1 | 0.865 | -16.1
B06 | 0 | 345 | 0.9 | 1.1 | 0.872 | -14.8
B07 | 0 | 345 | 0.9 | 1.1 | 0.838 | -16.3
B08 | 0 | 345 | 0.9 | 1.1 | 0.827 | -16.2
B09 | 0 | 345 | 0.9 | 1.1 | 0.733 | 1.5
B9_INV | 0 | 100 | 0.9 | 1.1 | 0.721 | 5.3
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L22 | B16 | B19 | 10.413 | 7.768 | 14.939
L14 | B08 | B09 | 6.999 | 5.976 | 8.963
L17 | B10 | B13 | 6.321 | 5.976 | 8.963
L07 | B04 | B05 | 7.688 | 5.976 | 8.963
L18 | B13 | B14 | 6.54 | 5.976 | 8.963
L09 | B05 | B06 | 8.195 | 5.976 | 8.963
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L30 | B25 | B26 | 0.176 | 2.988
L21 | B16 | B17 | 2.813 | 2.988
L31 | B26 | B27 | 2.325 | 2.988
L12 | B06 | B11 | 2.57 | 2.988
L32 | B26 | B28 | 1.478 | 2.988
L13 | B07 | B08 | 2.426 | 2.988
L23 | B16 | B21 | 1.772 | 2.988
L33 | B26 | B29 | 1.957 | 2.988
L03 | B02 | B03 | 2.908 | 2.988
L25 | B17 | B18 | 1.722 | 2.988
L16 | B10 | B11 | 2.864 | 2.988
L26 | B17 | B27 | 1.518 | 2.988
L06 | B03 | B18 | 0.416 | 2.988
L27 | B21 | B22 | 3.086 | 3.884
L08 | B04 | B14 | 2.842 | 2.988
L29 | B23 | B24 | 0.872 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
T03 | B06 | B31 | 913.116 | 800 | 850
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 378.919 | 550
T01 | B12 | B11 | 44.878 | 250
T02 | B12 | B13 | 56.432 | 250
T12 | B19 | B20 | 378.815 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]

## after step 04
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L22 | B16 | B19 | 10.327 | 7.768 | 14.939
L07 | B04 | B05 | 7.088 | 5.976 | 8.963
L18 | B13 | B14 | 6.16 | 5.976 | 8.963
L09 | B05 | B06 | 7.437 | 5.976 | 8.963
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B05 | B08 | 0.524 | 2.988
L20 | B15 | B16 | 2.355 | 2.988
L30 | B25 | B26 | 0.122 | 2.988
L11 | B06 | B07 | 2.603 | 2.988
L21 | B16 | B17 | 2.791 | 2.988
L31 | B26 | B27 | 2.219 | 2.988
L12 | B06 | B11 | 0.91 | 2.988
L32 | B26 | B28 | 1.445 | 2.988
L13 | B07 | B08 | 0.117 | 2.988
L23 | B16 | B21 | 1.462 | 2.988
L33 | B26 | B29 | 1.926 | 2.988
L03 | B02 | B03 | 2.102 | 2.988
L25 | B17 | B18 | 1.629 | 2.988
L16 | B10 | B11 | 1.304 | 2.988
L26 | B17 | B27 | 1.358 | 2.988
L06 | B03 | B18 | 0.076 | 2.988
L27 | B21 | B22 | 2.791 | 3.884
L08 | B04 | B14 | 2.52 | 2.988
L29 | B23 | B24 | 0.592 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
T03 | B06 | B31 | 866.169 | 800 | 850
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 344.981 | 550
T01 | B12 | B11 | 50.415 | 250
T02 | B12 | B13 | 49.097 | 250
T12 | B19 | B20 | 380.294 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]

## after step 05
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L22 | B16 | B19 | 10.314 | 7.768 | 14.939
L07 | B04 | B05 | 6.198 | 5.976 | 8.963
L09 | B05 | B06 | 6.626 | 5.976 | 8.963
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B05 | B08 | 0.619 | 2.988
L20 | B15 | B16 | 2.214 | 2.988
L30 | B25 | B26 | 0.184 | 2.988
L11 | B06 | B07 | 2.525 | 2.988
L21 | B16 | B17 | 2.492 | 2.988
L31 | B26 | B27 | 2.372 | 2.988
L12 | B06 | B11 | 1.525 | 2.988
L32 | B26 | B28 | 1.44 | 2.988
L13 | B07 | B08 | 0.118 | 2.988
L23 | B16 | B21 | 1.415 | 2.988
L33 | B26 | B29 | 1.921 | 2.988
L03 | B02 | B03 | 1.898 | 2.988
L04 | B02 | B25 | 2.969 | 2.988
L25 | B17 | B18 | 1.515 | 2.988
L16 | B10 | B11 | 1.84 | 2.988
L26 | B17 | B27 | 1.173 | 2.988
L06 | B03 | B18 | 0.108 | 2.988
L27 | B21 | B22 | 2.745 | 3.884
L08 | B04 | B14 | 2.553 | 2.988
L29 | B23 | B24 | 0.549 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 369.466 | 550
T01 | B12 | B11 | 48.393 | 250
T02 | B12 | B13 | 47.227 | 250
T12 | B19 | B20 | 380.571 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]

## after step 06
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
L22 | B16 | B19 | 10.233 | 7.768 | 14.939
L09 | B05 | B06 | 6.975 | 5.976 | 8.963
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B05 | B08 | 1.561 | 2.988
L20 | B15 | B16 | 1.163 | 2.988
L30 | B25 | B26 | 0.19 | 2.988
L11 | B06 | B07 | 2.451 | 2.988
L21 | B16 | B17 | 2.549 | 2.988
L31 | B26 | B27 | 2.261 | 2.988
L12 | B06 | B11 | 1.692 | 2.988
L32 | B26 | B28 | 1.402 | 2.988
L13 | B07 | B08 | 0.186 | 2.988
L23 | B16 | B21 | 1.079 | 2.988
L33 | B26 | B29 | 1.885 | 2.988
L03 | B02 | B03 | 0.726 | 2.988
L25 | B17 | B18 | 1.563 | 2.988
L16 | B10 | B11 | 1.781 | 2.988
L26 | B17 | B27 | 0.966 | 2.988
L06 | B03 | B18 | 0.525 | 2.988
L27 | B21 | B22 | 2.403 | 3.884
L08 | B04 | B14 | 2.592 | 2.988
L29 | B23 | B24 | 0.292 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 334.376 | 550
T01 | B12 | B11 | 50.846 | 250
T02 | B12 | B13 | 44.088 | 250
T12 | B19 | B20 | 383.235 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]

## after step 07
BUSES OUTSIDE VOLTAGE LIMITS ( 100 %)
Bus ID | Zone | kV Base | Vmin - [pu] | Vmax - [pu] | V sol - [pu] | Ang sol - [deg]
OVERLOADED LINES & CABLES ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu] | Emergency Loading Limit - [pu]
UNDERLOADED LINES & CABLES ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [pu] | Loading Limit - [pu]
L10 | B05 | B08 | 1.561 | 2.988
L20 | B15 | B16 | 1.163 | 2.988
L30 | B25 | B26 | 0.19 | 2.988
L11 | B06 | B07 | 2.451 | 2.988
L21 | B16 | B17 | 2.549 | 2.988
L31 | B26 | B27 | 2.261 | 2.988
L12 | B06 | B11 | 1.692 | 2.988
L32 | B26 | B28 | 1.402 | 2.988
L13 | B07 | B08 | 0.186 | 2.988
L23 | B16 | B21 | 1.079 | 2.988
L33 | B26 | B29 | 1.885 | 2.988
L03 | B02 | B03 | 0.726 | 2.988
L25 | B17 | B18 | 1.563 | 2.988
L16 | B10 | B11 | 1.781 | 2.988
L26 | B17 | B27 | 0.966 | 2.988
L06 | B03 | B18 | 0.525 | 2.988
L27 | B21 | B22 | 2.403 | 3.884
L08 | B04 | B14 | 2.592 | 2.988
L29 | B23 | B24 | 0.292 | 2.988
OVERLOADED TRANSFORMERS ( WITHIN 100 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA] | Emergency Loading Limit - [MVA]
UNDERLOADED TRANSFORMERS ( WITHIN 50 %)
ID | Bus From | Bus To | Power Flow - [MVA] | Loading Limit - [MVA]
T10 | B02 | B30 | 334.376 | 550
T01 | B12 | B11 | 50.846 | 250
T02 | B12 | B13 | 44.088 | 250
T12 | B19 | B20 | 383.235 | 550
GENERATORS AT REACTIVE LIMITS ( WITHIN 0 %)
ID | Bus From | P Gen - [MW] | Q Gen - [MVAR] | Q Min - [MVAR] | Q Max - [MVAR]
TRANSFORMERS AT TAP LIMITS ( WITHIN 0 %)
ID | Bus From | Bus To | Tap Pos - [%] | Min Tap - [%] | Max Tap - [%]